CITY OF CASEVILLE

6685 CLAY ST

CASEVILLE MI  48725

(989)856-4407

VOLUME 28, ISSUE 1                                                                                                                          WSSN 1190                                                                                                                              JANUARY 28, 2026

This report covers the drinking water quality for the City of Caseville Water Treatment Plant for the calendar year of 2025. Included are details about where your water comes from, what it contains, and how it compares to the Environmental Protection Agency (EPA) and State standards. Caseville Water Treatment Plant has buried intake located in Saginaw Bay.

The State performed an assessment of our source water in 2003. The source water area for the Caseville intake includes numerous listed potential contaminants sources in the Pigeon River watershed. Based on this the intake has a high degree of susceptibility to potential contaminant sources. The final assessment report is available for review at the Caseville City Hall.

Contaminants and their presence in water: Drinking Water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the EPA’s Safe Drinking Water Hot Line (1-800-426-4791).

Vulnerability of sub-populations: Some people may be more vulnerable to contaminants in drinking water than the general population. Immune-compromised people such as individuals with cancer undergoing chemotherapy, people who have undergone organ transplants, people with HIV/AIDS or other immune systems disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. The EPA/CDC guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (800-426-4791).

Sources of Drinking Water: The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. Our Water Treatment Plant treats surface water that comes from Saginaw Bay.  As water travels over the surface of the land or through the ground it dissolves naturally occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in your water include:

- Inorganic contaminants, such as salts and metals, which can naturally occur or result from urban storm water runoff.

- Pesticides and herbicides may come from a variety of sources such as agriculture and residential uses.

- Microbial contaminants, such as viruses and bacteria, may come from sewage treatment plants, septic systems, agricultural livestock operations and wildlife.

- Radioactive contaminants are naturally occurring.

- Organic chemical contaminants, including synthetic and volatile organic chemicals which are by-products of industrial process and petroleum production, and can also come from gas stations, urban storm water runoff, and septic systems.

We at the Caseville Water Treatment Plant are committed to providing you safe, reliable, and healthy water to every tap. We ask that all our customers help protect our water sources, which are the heart of our community, our way of life and our children's future. We are pleased to provide you with this information to keep you informed about your water quality. We will be updating this report annually, and we will also keep you informed of any problems that may occur throughout the year.

To ensure that tap water is safe to drink, EPA prescribes regulations which limit the amount of certain contaminants in water provided by public water systems. Food and Drug Administration regulations establish limits for contaminants in bottled water which provide the same protection for public health.  Is our water system meeting other rules that govern our operations? The State and EPA require us to test our water on a regular basis to ensure its safety. We passed all monitoring requirements for 2025.

Lead can cause serious health effects in people of all ages, especially pregnant people, infants (both formula-fed and breastfed), and young children. Lead in drinking water is primarily from materials and parts used in service lines and in home plumbing. Caseville Water Treatment Plant is responsible for providing high quality drinking water and removing lead pipes but cannot control the variety of materials used in the plumbing in your home. Because lead levels may vary over time, lead exposure is possible even when your tap sampling results do not detect lead at one point in time. You can help protect yourself and your family by identifying and removing lead materials within your home plumbing and taking steps to reduce your family's risk. Using a filter, certified by an American National Standards Institute accredited certifier to reduce lead, is effective in reducing lead exposures. Follow the instructions provided with the filter to ensure the filter is used properly. Use only cold water for drinking, cooking, and making baby formula. Boiling water does not remove lead from water. Before using tap water for drinking, cooking, or making baby formula, flush your pipes for several minutes. You can do this by running your tap, taking a shower, doing laundry or a load of dishes. If you have a lead service line or galvanized requiring replacement service line, you may need to flush your pipes for at least 5 minutes to flush water from both your home plumbing and the lead service line. If you are concerned about lead in your water and wish to have your water tested, contact Caseville Water Treatment Plant (989)856-4407. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available at https://www.epa.gov/safewater/lead.

Copper is an essential nutrient, but some people who drink water containing copper in excess of the action level over a relatively short amount of time could experience gastrointestinal distress. Some people who drink water containing copper in excess of the action level over many years could suffer liver or kidney damage.  People with Wilson’s disease should consult their personal doctor. City of Caseville will be conducting additional testing to acquire more information about copper concentrations in our water.

Customers can obtain a copy of this report at: https://casevillecity.com/notices/2026-water-quality-report/

Customers with questions or concerns about your water, or the contents of this report, contact Troy Hartz, Superintendent at (989)856-4407 or (989)963-0124. We want our valued customers to be informed about their water utility. If you want to learn more, please attend any of our regularly scheduled City Council meetings. They are conducted in the Conference room, at the City/Township Hall on the second Monday of each month at 5:30 p.m.

## The tables below list all the drinking water contaminants that we detected during the 2025 calendar year. The presence of these contaminants in the water does not necessarily indicate that the water poses a health risk. Unless otherwise noted, the data present in this table is done January 1 through December 31, 2025. The State allows us to monitor certain contaminants less than once per year because the concentration levels of these contaminants are not expected to vary significantly from year to year. All the data is representative of the water quality, but some data is more than one year old.

## Terms and abbreviations used in the tables below:

- Maximum Contaminant Level Goal (MCLG): The level of contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.

- Maximum Contaminant Level (MCL): The highest level of contaminant that is allowed in drinking water.  MCLs are set as close to MCLGs as feasible using the best available treatment technology.

- Action Level (AL): The concentration of a contaminant which, when exceeded, triggers treatment or other requirements which a water system must follow.

- ppm: parts per million or milligrams per liter: One part per million corresponds to one minute in two years or a single penny in $10,000.

- ppb: parts per billion or micrograms per liter: 1 part per billion corresponds to 1 minute in 2000 years, or a single penny in $10,000,000.

- ppt: parts per trillion or nanograms per liter: 1 part per trillion is equivalent to a single penny in $10,000,000,000.

- N/D: not detectable at testing limit

- N/A: not applicable

- Treatment Technique (TT): A treatment technique is a required process intended to reduce the level of a specific contaminant in drinking water.

- pCi/L or picocuries per liter: a measure of radioactivity

- NTU: Turbidity is measured in Nephelometric Turbidity Units

## Running Annual Average Distribution Chlorine (RAA)

## Highest RAA = 1.34 ppm

## Range Low    = 0.86 ppm

Range High   = 1.60 ppm

| CONTAMINANT | MCL | MCLG | OUR WATER | RANGE OF DETECTION | VIOLATION | TYPICAL SOURCE OF CONTAMNANT |
| --- | --- | --- | --- | --- | --- | --- |
| TURBIDITY * | 1 NTU | .30 NTU | .05 NTU | .03 to .05 NTU | N | Soil run off. Daily Testing |
| FLUORIDE | 4 ppm | 4 ppm | .14 ppm | N/A | N | Erosion and natural deposits: water additive which promotes strong teeth. 8/21/2025 |
| COPPER | AL= 1.3 ppm | 1.3 ppm | 1.10 ppm | .2 to 1.2 ppm *** | N | Corrosion of household plumbing systems. 8/11/2025 - 8/15/2025 |
| LEAD | AL=12 ppb | N/A | 7 ppb | 0 to 15 ppb ** | N | Lead service lines, corrosion of household plumbing including fittings and fixtures. Erosion of natural deposits. 8/11/2025-8/15/2025 |
| TOTAL TRIHALOMETHANE | 80 ppb | 0 ppb | 35 ppb | 19 to 50 ppb | N | By-product of drinking water chlorination 2025 Collection dates 2/3, 5/20, 8/27, 11/05 |
| TOTAL (5 TOTAL) HALOACETIC ACIDS | 60 ppb | 0 ppb | 18 ppb | 12 to 30 ppb | N | By-product of drinking water chlorination 2025 Collection dates 2/3, 5/20, 8/27, 11/05 |
| BARIUM | 2000 ppb | 0 ppb | 20 ppb | N/A | N | Erosion of natural deposits. 4/27/2021 |
| SELENIUM | 50 ppb | 0 ppb | 1 ppb | N/A | N | Erosion of natural deposits. 4/27/2021 |
| ARSENIC | 10 ppb | 0 ppb | ND | N/A | N | Erosion of natural deposits. 4/27/2021 |
| NITRATE | 10 ppm | 0 ppm | ND | N/A | N | Run off from fertilizer use. 8/21/2025 |
| RADIOLOGICAL |  |  |  |  |  |  |
| URANIUM | .03 ppm | 0 ppm | .0003 ppm | .0003 ppm | N | Erosion of natural deposits. 9/17/2024 |
| GROSS ALPHA RADIUM 226 – 228 | 15 pCi / L | 0 pCi / L | ND | N/A | N | Erosion of natural deposits. 4/11/2023 |
| COMBINED | 5 pCi / L | 0 pCi / L | ND | N/A | N | Erosion of natural deposits. 4/11/2023 |
| NOT REGULATED |  |  |  |  |  |  |
| SODIUM | N/A | N/A | 14 ppm | N/A | N | Erosion of natural deposits. 8/21/2025 |
| MANGANESE **** | N/A | N/A | .06 ppm | .06 ppm | N | Natural, industrial, and agricultural contaminants 8/25/2025 |
| ZINC | N/A | N/A | .01 ppm | .01 ppm | N | Erosion of natural deposits. 6/11/2025 |
| IRON | N/A | N/A | .08 ppm | .08 ppm | N | Erosion of natural deposits. 6/11/2025 |
| CHLORIDE | N/A | N/A | 20 ppm | N/A | N | Erosion of natural deposits. 8/21/2025 |
| SULFATE | N/A | N/A | 170 ppm | N/A | N | Naturally occurring. 8/21/2025 |
| MICROBIAL CONTAMINANTS NONE DETECTED IN 2025 |  |  |  |  |  |  |

* 100% OF NTU SAMPLES ANALYZED MET THE CRITERIA FOR THE MCL LEVEL

** TEN LEAD SAMPLES WERE TAKEN DURING 2025 AND ONE SAMPLE EXCEEDED THE ACTION LEVEL. :   THE 90TH PERCENTILE RESULT WAS 7 ppb.  ONE SAMPLE TESTED ABOVE THE ACTION LEVEL OF 12 ppb AT 15 ppb.  FOLLOW UP INVESTAGATORY SAMPLES WERE TAKEN AT THE ADDRESS THAT TESTED ABOVE THE ACTION LEVEL AND IT WAS DETERMINED THAT ONE OF THE FIXTURES OR PLUMBING DIRECTLEY CONNECTED TO THE FIXTURE WAS THE SOURCE OF THE ELEVATED LEAD LEVEL.  IT IS IMPORTANT TO CONSIDER THE FOLLOWING STATEMENT:

There is no safe level of lead in drinking water.  Exposure to lead in drinking water can cause serious health effects in all age groups.  Infants and children can have decreases in IQ and attention span.  Lead exposure can lead to new learning and behavior problems or exacerbate existing learning and behavior problems.  The children of persons who are exposed to lead before or during pregnancy can have increased risk of these adverse health effects.  Adults can have increased risks of heart disease, high blood pressure, kidney or nervous system problems.

In 2024 162 services out of 806 services were inspected and NO lead was found.

*** TEN COPPER SAMPLES WERE TAKEN AND NO SAMPLES EXCEEDED THE ACTION LEVEL: THE 90TH PERCENTILE RESULT WAS 1.10 ppm

**** Manganese has a secondary MCL of .05 ppm, at this level it may cause aesthetic concerns for color, staining, odor, and taste.  A lifetime health advisory of .3 ppm is recommended by the US EPA for all drinking water.  Short-term health advisory advises the general public to limit intake to 1.0 ppm for no more that 10 days.

PFAS

Per- and polyfluoroalkyl substances (PFAS) are a large group of manmade chemicals that are resistant to heat, water, and oil. For decades, they have been used in many industrial applications and consumer products such as carpeting, waterproof clothing, upholstery, food paper wrappings, personal care products, fire-fighting foams, and metal plating. PFAS are prevalent and have been found in the environment all over the world.

| CONTAMINANT Per and polyfluoroalkyl substances (PFAS) | MCL | MCLG | OUR WATER | RANGE OF DETECTION | VIOLATION | TYPICAL SOURCE OF CONTAMNANT |
| --- | --- | --- | --- | --- | --- | --- |
| Hexafluoropropylene Oxide dimer acid (HFPO-DA) | 370 ppt | N/A | N/D | N/A | N | Discharge and waste from industrial facilities utilizing the Gen X chemical process Date collected 08/21/2025 Collected |
| Perfluorobutane Sulfonic acid (PFBS) | 420 ppt | N/A | N/D | N/A | N | Discharge and waste from industrial facilities; stain-resistant treatments Date collected 08/21/2025 |
| Perfluorohexane Sulfonic acid (PFHxS) | 51 ppt | N/A | N/D | N/A | N | Firefighting foam; discharge and waste from industrial facilities Date collected 08/21/2025 |
| Perfluorohexanoic Acid (PFHxA) | 400,000 ppt | N/A | N/D | N/A | N | Firefighting foam; discharge and waste from industrial facilities Date collected 08/21/2025 |
| Perfluorononanoic Acid (PFNA) | 6 ppt | N/A | N/D | N/A | N | Discharge and waste from industrial facilities; breakdown of precursor compounds Date collected 08/21/2025 |
| Perfluorooctane Sulfonic acid (PFOS) | 16 ppt | N/A | N/D | N/A | N | Firefighting foam; discharge from electroplating facilities; discharge and waste from industrial facilities Date collected 08/21/2025 |
| Perfluorooctanoic Acid (PFOA) | 8 ppt | N/A | 3 ppt | N/A | N | Discharge and waste from industrial facilities; stain-resistant treatments Date collected 08/21/2025 |